| ## WEEKLY LOG SHEETS |  |  |
| --- | --- | --- |
| ### RARELY USED OUTLETS E.g. taps, WC’s |  |  |
| - Flush all infrequently used hot and cold water outlets for at least 2 minutes to remove any stagnant water in the system. Please note: ‘infrequently used outlets’ may be defined as outlets that have not been used within the last seven days. - Record in the comments section time and dates that flushing procedures were completed and sign entry. |  |  |
| LOCATION | FLUSHED FOR 2 MINUTES | COMMENTS |
| DATE SIGNED |  |  |

|  | ## WEEKLY LOG SHEETS |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | ## SHOWERS AND SPECIALIST BATHS ### E.g. argo, parker, medic, etc |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | - Flush all showers (inclusive of all shower attachments to specialist baths) for at least 2 minutes and run to drain. - Run the hot and cold taps to the baths for at least 2 minutes. - Record in the comments section the time and dates that flushing procedures were completed and sign entry. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | LOCATION |  |  |  |  |  |  |  |  |  |  |  | FLUSHED FOR 2 MINUTES |  |  |  |  | COMMENTS |  |  |  |  |
|  | DATE SIGNED |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| #### MONTHLY LOG SHEET |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Check that the water temperature at the nearest and furthest cold water outlets to the cold water storage tank is below 20oC after running the water for 2 minutes. Report any temperatures above 20 OC to Property Services |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ##### COLD TAP FURTHEST FROM COLD WATER STORAGE TANK |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | LOCATION |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | FLUSHED 2 MINUTE |  |  |  |  |  |  |  |  |  |  |  |  |  | (YES) TICK (NO) CROSS |  |  |  |  |  |  |
|  |  | CHECK TEMPERATURE |  |  |  |  |  |  |  |  |  |  |  | OC |  | RECORD TEMPERATURE |  |  |  |  |  |  |
| ##### COLD TAP NEAREST TO COLD WATER STORAGE TANK |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | LOCATION |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | FLUSHED 2 MINUTE |  |  |  |  |  |  |  |  |  |  |  |  |  | (YES) TICK (NO) CROSS |  |  |  |  |  |  |
|  |  | CHECK TEMPERATURE |  |  |  |  |  |  |  |  |  |  |  | OC |  | RECORD TEMPERATURE |  |  |  |  |  |  |
| ##### COLD TAP FURTHEST FROM COLD WATER STORAGE TANK |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | LOCATION |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | FLUSHED 2 MINUTE |  |  |  |  |  |  |  |  |  |  |  |  |  | (YES) TICK (NO) CROSS |  |  |  |  |  |  |
|  |  | CHECK TEMPERATURE |  |  |  |  |  |  |  |  |  |  |  | OC |  | RECORD TEMPERATURE |  |  |  |  |  |  |
| ##### COLD TAP NEAREST TO COLD WATER STORAGE TANK |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | LOCATION |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | FLUSHED 2 MINUTE |  |  |  |  |  |  |  |  |  |  |  |  |  | (YES) TICK (NO) CROSS |  |  |  |  |  |  |
|  |  | CHECK TEMPERATURE |  |  |  |  |  |  |  |  |  |  |  | OC |  | RECORD TEMPERATURE |  |  |  |  |  |  |
| ##### COLD TAP FURTHEST FROM COLD WATER STORAGE TANK |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | LOCATION |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | FLUSHED 2 MINUTE |  |  |  |  |  |  |  |  |  |  |  |  |  | (YES) TICK (NO) CROSS |  |  |  |  |  |  |
|  |  | CHECK TEMPERATURE |  |  |  |  |  |  |  |  |  |  |  | OC |  | RECORD TEMPERATURE |  |  |  |  |  |  |
| ##### COLD TAP NEAREST TO COLD WATER STORAGE TANK |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | LOCATION |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | FLUSHED 2 MINUTE |  |  |  |  |  |  |  |  |  |  |  |  | (YES) TICK (NO) CROSS |  |  |  |  |  |  |  |
|  |  | CHECK TEMPERATURE |  |  |  |  |  |  |  |  |  |  |  | OC | RECORD TEMPERATURE |  |  |  |  |  |  |  |
|  |  | DATE |  |  |  |  |  |  |  |  |  | SIGNATURE |  |  |  |  |  |  |  |  |  |  |

| #### MONTHLY LOG SHEET |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ##### Check that the water temperatures at the nearest and furthest hot water outlets to the calorifier (cylinder) is at least 50 oC within 1 minute of running the water. ##### If a thermostatic mixing valve (TMV) is fitted to an outlet, the temperature should be measured at the point in the system immediately before the TMV. - Report any temperatures below 50 oC to Property Services. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ##### HOT TAP FURTHEST FROM CALORIFIER |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | LOCATION |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | FLUSHED FOR 1 MINUTE |  |  |  |  |  |  |  | TICK FOR YES |  |  |  |  |  |
|  | CHECK TEMPERATURE |  |  |  |  |  |  | OC |  |  |  |  |  |  |
| ##### HOT TAP NEAREST TO CALORIFIER |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | LOCATION |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | FLUSHED FOR 1 MINUTE |  |  |  |  |  |  |  | TICK FOR YES |  |  |  |  |  |
|  | CHECK TEMPERATURE |  |  |  |  |  |  | OC |  |  |  |  |  |  |
| ##### HOT TAP FURTHEST FROM CALORIFIER |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | LOCATION |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | FLUSHED FOR 1 MINUTE |  |  |  |  |  |  |  | TICK FOR YES |  |  |  |  |  |
|  | CHECK TEMPERATURE |  |  |  |  |  |  | OC |  |  |  |  |  |  |
| ##### HOT TAP NEAREST TO CALORIFIER |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | LOCATION |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | FLUSHED FOR 1 MINUTE |  |  |  |  |  |  |  | TICK FOR YES |  |  |  |  |  |
|  | CHECK TEMPERATURE |  |  |  |  |  |  | OC |  |  |  |  |  |  |
|  |  |  | DATE |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | SIGNATURE |  |  |  |  |  |  |  |  |  |  |  |

WORK REPORT SHEET

SITE ADDRESS

DETAILS OF WORK CARRIED OUT

COMPANY NAME

PRINTED NAME

SIGNATURE OF RESPONSIBLE PERSON

SIGNATURE

DATE